## Processing_Summary
Statistic | Value
Total Files Processed | 5
Successfully Processed | 5
Failed Files | 0
Failure Rate (%) | 0
Failed Files List | None

## summary
SourceFile | Raw_Feed_#number | Raw_Feed_Description | Raw_Feed_Flow | Raw_Feed_TDS | Raw_Feed_Pressure | Net_Feed_#number | Net_Feed_Description | Net_Feed_Flow | Net_Feed_TDS | Net_Feed_Pressure | Total_Conc_#number | Total_Conc_Description | Total_Conc_Flow | Total_Conc_TDS | Total_Conc_Pressure | Net_Product_#number | Net_Product_Description | Net_Product_Flow | Net_Product_TDS | Net_Product_Pressure
WAVE_Report_PV1_ELS1_Pressure20.xls | 1 | Raw Feed to RO System | 2.10 | 10,001 | 0.0 | 2 | Net Feed to Pass 1 | 2.10 | 10,010 | 20.0 | 4 | Total Concentrate from Pass 1 | 1.63 | 12,805 | 19.4 | 6 | Net Product from RO System | 0.47 | 363.3 | 0.0
WAVE_Report_PV1_ELS2_Pressure10.xls | 1 | Raw Feed to RO System | 2.10 | 10,001 | 0.0 | 2 | Net Feed to Pass 1 | 2.10 | 10,005 | 10.0 | 4 | Total Concentrate from Pass 1 | 1.85 | 11,244 | 9.1 | 6 | Net Product from RO System | 0.25 | 906.3 | 0.0
WAVE_Report_PV1_ELS2_Pressure20.xls | 1 | Raw Feed to RO System | 2.10 | 10,001 | 0.0 | 2 | Net Feed to Pass 1 | 2.10 | 10,010 | 20.0 | 4 | Total Concentrate from Pass 1 | 1.28 | 16,114 | 19.2 | 6 | Net Product from RO System | 0.82 | 455.8 | 0.0
WAVE_Report_PV1_ELS3_Pressure10.xls | 1 | Raw Feed to RO System | 2.10 | 10,001 | 0.0 | 2 | Net Feed to Pass 1 | 2.10 | 10,005 | 10.0 | 4 | Total Concentrate from Pass 1 | 1.76 | 11,753 | 8.9 | 6 | Net Product from RO System | 0.34 | 1,007 | 0.0
WAVE_Report_PV1_ELS3_Pressure20.xls | 1 | Raw Feed to RO System | 2.10 | 10,001 | 0.0 | 2 | Net Feed to Pass 1 | 2.10 | 10,010 | 20.0 | 4 | Total Concentrate from Pass 1 | 1.04 | 19,593 | 19.1 | 6 | Net Product from RO System | 1.06 | 568.5 | 0.0

## system_overview
SourceFile | Trains | Online | Standby | RORecovery | NetFeed | NetProduct
WAVE_Report_PV1_ELS1_Pressure20.xls | 1 | 1.0 | 0.0 | 22.5 % | 2.1 | 0.47
WAVE_Report_PV1_ELS2_Pressure10.xls | 1 | 1.0 | 0.0 | 12.0 % | 2.1 | 0.25
WAVE_Report_PV1_ELS2_Pressure20.xls | 1 | 1.0 | 0.0 | 39.0 % | 2.1 | 0.82
WAVE_Report_PV1_ELS3_Pressure10.xls | 1 | 1.0 | 0.0 | 16.3 % | 2.1 | 0.34
WAVE_Report_PV1_ELS3_Pressure20.xls | 1 | 1.0 | 0.0 | 50.4 % | 2.1 | 1.06

## pass_details
SourceFile | Pass | Stream Name | Water Type | Number of Elements | Total Active Area | Feed Flow per Pass | Feed TDSᵃ | Feed Pressure | Flow Factor Per Stage | Permeate Flow per Pass | Pass Average flux | Permeate TDSᵃ | Pass Recovery | Average NDP | Specific Energy | Temperature | pH | Chemical Dose | RO System Recovery | Net RO System Recovery
WAVE_Report_PV1_ELS1_Pressure20.xls | Pass 1 | IO+B_10,000_2 | Well Water (SDI < 3) | 1 | 7.62 | 2.10 | 10,010 | 20.0 | 0.85 | 0.47 | 61.9 | 363.3 | 22.4 % | 11.8 | 3.11 | 25.0 | 7.9 | - | 22.5 % | 22.5%
WAVE_Report_PV1_ELS2_Pressure10.xls | Pass 1 | IO+B_10,000_2 | Well Water (SDI < 3) | 2 | 15.2 | 2.10 | 10,005 | 10.0 | 0.85 | 0.25 | 16.5 | 906.3 | 11.9 % | 2.6 | 2.92 | 25.0 | 7.9 | - | 12.0 % | 12.0%
WAVE_Report_PV1_ELS2_Pressure20.xls | Pass 1 | IO+B_10,000_2 | Well Water (SDI < 3) | 2 | 15.2 | 2.10 | 10,010 | 20.0 | 0.85 | 0.82 | 53.7 | 455.8 | 39.0 % | 10.6 | 1.78 | 25.0 | 7.9 | - | 39.0 % | 39.0%
WAVE_Report_PV1_ELS3_Pressure10.xls | Pass 1 | IO+B_10,000_2 | Well Water (SDI < 3) | 3 | 22.9 | 2.10 | 10,005 | 10.0 | 0.85 | 0.34 | 15.0 | 1,007 | 16.2 % | 2.3 | 2.15 | 25.0 | 7.9 | - | 16.3 % | 16.3%
WAVE_Report_PV1_ELS3_Pressure20.xls | Pass 1 | IO+B_10,000_2 | Well Water (SDI < 3) | 3 | 22.9 | 2.10 | 10,010 | 20.0 | 0.85 | 1.06 | 46.3 | 568.5 | 50.5 % | 9.4 | 1.38 | 25.0 | 7.9 | - | 50.4 % | 50.4%

## stage_flow
SourceFile | Stage | ElementType | PV | ElsPer | Feed_Flow | Feed_Recirc | Feed_Press | Feed_Boost_Press | Conc_Flow | Conc_Press | Conc_Press_Drop | Perm_Flow | Perm_Avg_Flux | Perm_Press | Perm_TDS
WAVE_Report_PV1_ELS1_Pressure20.xls | 1 | NF90-4040 | 1 | 1 | 2.10 | 0.00 | 19.7 | 0.0 | 1.63 | 19.4 | 0.3 | 0.47 | 61.9 | 0.0 | 363.3
WAVE_Report_PV1_ELS2_Pressure10.xls | 1 | NF90-4040 | 1 | 2 | 2.10 | 0.00 | 9.7 | 0.0 | 1.85 | 9.1 | 0.6 | 0.25 | 16.5 | 0.0 | 906.3
WAVE_Report_PV1_ELS2_Pressure20.xls | 1 | NF90-4040 | 1 | 2 | 2.10 | 0.00 | 19.7 | 0.0 | 1.28 | 19.2 | 0.5 | 0.82 | 53.7 | 0.0 | 455.8
WAVE_Report_PV1_ELS3_Pressure10.xls | 1 | NF90-4040 | 1 | 3 | 2.10 | 0.00 | 9.7 | 0.0 | 1.76 | 8.9 | 0.8 | 0.34 | 15.0 | 0.0 | 1,007
WAVE_Report_PV1_ELS3_Pressure20.xls | 1 | NF90-4040 | 1 | 3 | 2.10 | 0.00 | 19.7 | 0.0 | 1.04 | 19.1 | 0.6 | 1.06 | 46.3 | 0.0 | 568.5

## solute_concentrations
SourceFile | NH₄⁺_Feed | NH₄⁺_Stage1_Conc | NH₄⁺_Stage1_Prem | NH₄⁺_Total | K⁺_Feed | K⁺_Stage1_Conc | K⁺_Stage1_Prem | K⁺_Total | Na⁺_Feed | Na⁺_Stage1_Conc | Na⁺_Stage1_Prem | Na⁺_Total | Mg⁺²_Feed | Mg⁺²_Stage1_Conc | Mg⁺²_Stage1_Prem | Mg⁺²_Total | Ca⁺²_Feed | Ca⁺²_Stage1_Conc | Ca⁺²_Stage1_Prem | Ca⁺²_Total | Sr⁺²_Feed | Sr⁺²_Stage1_Conc | Sr⁺²_Stage1_Prem | Sr⁺²_Total | Ba⁺²_Feed | Ba⁺²_Stage1_Conc | Ba⁺²_Stage1_Prem | Ba⁺²_Total | CO₃⁻²_Feed | CO₃⁻²_Stage1_Conc | CO₃⁻²_Stage1_Prem | CO₃⁻²_Total | HCO₃⁻_Feed | HCO₃⁻_Stage1_Conc | HCO₃⁻_Stage1_Prem | HCO₃⁻_Total | NO₃⁻_Feed | NO₃⁻_Stage1_Conc | NO₃⁻_Stage1_Prem | NO₃⁻_Total | F⁻_Feed | F⁻_Stage1_Conc | F⁻_Stage1_Prem | F⁻_Total | Cl⁻_Feed | Cl⁻_Stage1_Conc | Cl⁻_Stage1_Prem | Cl⁻_Total | Br⁻¹_Feed | Br⁻¹_Stage1_Conc | Br⁻¹_Stage1_Prem | Br⁻¹_Total | SO₄⁻²_Feed | SO₄⁻²_Stage1_Conc | SO₄⁻²_Stage1_Prem | SO₄⁻²_Total | PO₄⁻³_Feed | PO₄⁻³_Stage1_Conc | PO₄⁻³_Stage1_Prem | PO₄⁻³_Total | SiO₂_Feed | SiO₂_Stage1_Conc | SiO₂_Stage1_Prem | SiO₂_Total | Boron_Feed | Boron_Stage1_Conc | Boron_Stage1_Prem | Boron_Total | CO₂_Feed | CO₂_Stage1_Conc | CO₂_Stage1_Prem | CO₂_Total | TDS_Feed | TDS_Stage1_Conc | TDS_Stage1_Prem | TDS_Total | Cond._Feed | Cond._Stage1_Conc | Cond._Stage1_Prem | Cond._Total | pH_Feed | pH_Stage1_Conc | pH_Stage1_Prem | pH_Total
WAVE_Report_PV1_ELS1_Pressure20.xls | 0.00 | 0.00 | 0.00 | 0.00 | 123.0 | 157.2 | 5.43 | 5.43 | 3,068 | 3,921 | 136.4 | 136.4 | 355.0 | 458.0 | 0.87 | 0.87 | 117.0 | 151.0 | 0.32 | 0.32 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.36 | 2.04 | 0.00 | 0.00 | 54.08 | 69.27 | 0.25 | 0.25 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 5,469 | 6,997 | 216.8 | 216.8 | 16.00 | 20.39 | 0.91 | 0.91 | 780.0 | 1,007 | 1.45 | 1.45 | 0.00 | 0.00 | 0.00 | 0.00 | 16.00 | 20.55 | 0.36 | 0.36 | 1.03 | 1.17 | 0.52 | 0.52 | 0.57 | 0.71 | 0.50 | 0.50 | 10,001 | 12,805 | 363.3 | 363.3 | 16,983 | 21,231 | 743 | 743 | 7.9 | 7.9 | 5.8 | 5.8
WAVE_Report_PV1_ELS2_Pressure10.xls | 0.00 | 0.00 | 0.00 | 0.00 | 123.0 | 137.8 | 14.53 | 14.53 | 3,068 | 3,441 | 340.1 | 340.1 | 355.0 | 403.2 | 2.04 | 2.04 | 117.0 | 132.9 | 0.77 | 0.77 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.36 | 1.67 | 0.00 | 0.00 | 54.08 | 61.19 | 0.45 | 0.45 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 5,469 | 6,143 | 541.3 | 541.3 | 16.00 | 17.88 | 2.22 | 2.22 | 780.0 | 886.1 | 3.26 | 3.26 | 0.00 | 0.00 | 0.00 | 0.00 | 16.00 | 18.05 | 0.97 | 0.97 | 1.03 | 1.07 | 0.73 | 0.73 | 0.57 | 0.62 | 0.53 | 0.53 | 10,001 | 11,244 | 906.3 | 906.3 | 16,983 | 18,878 | 1,805 | 1,805 | 7.9 | 7.9 | 6.0 | 6.0
WAVE_Report_PV1_ELS2_Pressure20.xls | 0.00 | 0.00 | 0.00 | 0.00 | 123.0 | 197.4 | 6.88 | 6.88 | 3,068 | 4,924 | 171.1 | 171.1 | 355.0 | 581.7 | 1.09 | 1.09 | 117.0 | 191.7 | 0.40 | 0.40 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.36 | 2.98 | 0.00 | 0.00 | 54.08 | 87.30 | 0.29 | 0.29 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 5,469 | 8,798 | 272.1 | 272.1 | 16.00 | 25.52 | 1.14 | 1.14 | 780.0 | 1,278 | 1.80 | 1.80 | 0.00 | 0.00 | 0.00 | 0.00 | 16.00 | 25.96 | 0.45 | 0.45 | 1.03 | 1.31 | 0.58 | 0.58 | 0.57 | 0.90 | 0.56 | 0.56 | 10,001 | 16,114 | 455.8 | 455.8 | 16,983 | 26,095 | 927 | 927 | 7.9 | 7.8 | 5.8 | 5.8
WAVE_Report_PV1_ELS3_Pressure10.xls | 0.00 | 0.00 | 0.00 | 0.00 | 123.0 | 143.8 | 16.16 | 16.16 | 3,068 | 3,592 | 377.7 | 377.7 | 355.0 | 423.7 | 2.30 | 2.30 | 117.0 | 139.6 | 0.87 | 0.87 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.36 | 1.81 | 0.00 | 0.00 | 54.08 | 64.20 | 0.50 | 0.50 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 5,469 | 6,418 | 601.2 | 601.2 | 16.00 | 18.64 | 2.45 | 2.45 | 780.0 | 931.3 | 3.66 | 3.66 | 0.00 | 0.00 | 0.00 | 0.00 | 16.00 | 18.91 | 1.08 | 1.08 | 1.03 | 1.08 | 0.75 | 0.75 | 0.57 | 0.65 | 0.55 | 0.55 | 10,001 | 11,753 | 1,007 | 1,007 | 16,983 | 19,647 | 1,997 | 1,997 | 7.9 | 7.9 | 6.0 | 6.0
WAVE_Report_PV1_ELS3_Pressure20.xls | 0.00 | 0.00 | 0.00 | 0.00 | 123.0 | 239.3 | 8.66 | 8.66 | 3,068 | 5,971 | 213.4 | 213.4 | 355.0 | 714.6 | 1.36 | 1.36 | 117.0 | 235.5 | 0.50 | 0.50 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 1.36 | 4.11 | 0.00 | 0.00 | 54.08 | 106.5 | 0.34 | 0.34 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 5,469 | 10,686 | 339.4 | 339.4 | 16.00 | 30.83 | 1.42 | 1.42 | 780.0 | 1,571 | 2.24 | 2.24 | 0.00 | 0.00 | 0.00 | 0.00 | 16.00 | 31.69 | 0.57 | 0.57 | 1.03 | 1.43 | 0.64 | 0.64 | 0.57 | 1.13 | 0.62 | 0.62 | 10,001 | 19,593 | 568.5 | 568.5 | 16,983 | 31,064 | 1,149 | 1,149 | 7.9 | 7.8 | 5.9 | 5.9

## design_warnings
SourceFile | RO Design Warnings | Content
WAVE_Report_PV1_ELS1_Pressure20.xls | Design Warning: Permeate Flow Rate > Maximum Limit Limit: 0.29 Value: 0.47 Pass: 1 Stage: 1 Element: 1 Product: NF90-4040 Design Warning: Element Recovery > Maximum Limit Limit: 19.0 Value: 22.5 Pass: 1 Stage: 1 Element: 1 Product: NF90-4040
WAVE_Report_PV1_ELS2_Pressure10.xls |  | No design warnings found
WAVE_Report_PV1_ELS2_Pressure20.xls | Design Warning: Permeate Flow Rate > Maximum Limit Limit: 0.29 Value: 0.47 Pass: 1 Stage: 1 Element: 1 Product: NF90-4040 Design Warning: Permeate Flow Rate > Maximum Limit Limit: 0.29 Value: 0.35 Pass: 1 Stage: 1 Element: 2 Product: NF90-4040 Design Warning: Element Recovery > Maximum Limit Limit: 19.0 Value: 22.5 Pass: 1 Stage: 1 Element: 1 Product: NF90-4040 Design Warning: Element Recovery > Maximum Limit Limit: 19.0 Value: 21.3 Pass: 1 Stage: 1 Element: 2 Product: NF90-4040
WAVE_Report_PV1_ELS3_Pressure10.xls |  | No design warnings found
WAVE_Report_PV1_ELS3_Pressure20.xls | Design Warning: Permeate Flow Rate > Maximum Limit Limit: 0.29 Value: 0.47 Pass: 1 Stage: 1 Element: 1 Product: NF90-4040 Design Warning: Permeate Flow Rate > Maximum Limit Limit: 0.29 Value: 0.35 Pass: 1 Stage: 1 Element: 2 Product: NF90-4040 Design Warning: Element Recovery > Maximum Limit Limit: 19.0 Value: 22.5 Pass: 1 Stage: 1 Element: 1 Product: NF90-4040 Design Warning: Element Recovery > Maximum Limit Limit: 19.0 Value: 21.3 Pass: 1 Stage: 1 Element: 2 Product: NF90-4040

## element_flow
SourceFile | row_1_Stage | row_1_Element | row_1_Element_Name | row_1_Recovery | row_1_Feed_Flow | row_1_Feed_Press | row_1_Feed_TDS | row_1_Conc_Flow | row_1_Perm_Flow | row_1_Perm_Flux | row_1_Perm_TDS | row_2_Stage | row_2_Element | row_2_Element_Name | row_2_Recovery | row_2_Feed_Flow | row_2_Feed_Press | row_2_Feed_TDS | row_2_Conc_Flow | row_2_Perm_Flow | row_2_Perm_Flux | row_2_Perm_TDS | row_3_Stage | row_3_Element | row_3_Element_Name | row_3_Recovery | row_3_Feed_Flow | row_3_Feed_Press | row_3_Feed_TDS | row_3_Conc_Flow | row_3_Perm_Flow | row_3_Perm_Flux | row_3_Perm_TDS
WAVE_Report_PV1_ELS1_Pressure20.xls | 1 | 1 | NF90-4040 | 22.5 | 2.10 | 19.7 | 10,009 | 1.63 | 0.47 | 61.9 | 363.3
WAVE_Report_PV1_ELS2_Pressure10.xls | 1 | 1 | NF90-4040 | 6.7 | 2.10 | 9.7 | 10,005 | 1.96 | 0.14 | 18.4 | 808.8 | 1 | 2 | NF90-4040 | 5.7 | 1.96 | 9.4 | 10,661 | 1.85 | 0.11 | 14.7 | 1,028
WAVE_Report_PV1_ELS2_Pressure20.xls | 1 | 1 | NF90-4040 | 22.5 | 2.10 | 19.7 | 10,009 | 1.63 | 0.47 | 61.9 | 363.3 | 1 | 2 | NF90-4040 | 21.3 | 1.63 | 19.4 | 12,805 | 1.28 | 0.35 | 45.6 | 581.7
WAVE_Report_PV1_ELS3_Pressure10.xls | 1 | 1 | NF90-4040 | 6.7 | 2.10 | 9.7 | 10,005 | 1.96 | 0.14 | 18.4 | 808.8 | 1 | 2 | NF90-4040 | 5.7 | 1.96 | 9.4 | 10,661 | 1.85 | 0.11 | 14.7 | 1,028 | 1 | 3 | NF90-4040 | 4.9 | 1.85 | 9.1 | 11,244 | 1.76 | 0.09 | 11.8 | 1,287
WAVE_Report_PV1_ELS3_Pressure20.xls | 1 | 1 | NF90-4040 | 22.5 | 2.10 | 19.7 | 10,009 | 1.63 | 0.47 | 61.9 | 363.3 | 1 | 2 | NF90-4040 | 21.3 | 1.63 | 19.4 | 12,805 | 1.28 | 0.35 | 45.6 | 581.7 | 1 | 3 | NF90-4040 | 18.7 | 1.28 | 19.2 | 16,114 | 1.04 | 0.24 | 31.4 | 954.4

## solubility_warnings
SourceFile | Content
WAVE_Report_PV1_ELS1_Pressure20.xls | No solubility warnings found
WAVE_Report_PV1_ELS2_Pressure10.xls | No solubility warnings found
WAVE_Report_PV1_ELS2_Pressure20.xls | No solubility warnings found
WAVE_Report_PV1_ELS3_Pressure10.xls | No solubility warnings found
WAVE_Report_PV1_ELS3_Pressure20.xls | No solubility warnings found

## chemical_adjustments
SourceFile | pH_Pass_1_Feed | pH_RO_Pass_1_Conc | Langelier_Saturation_Index_Pass_1_Feed | Langelier_Saturation_Index_RO_Pass_1_Conc | Stiff_&_Davis_Stability_Index_Pass_1_Feed | Stiff_&_Davis_Stability_Index_RO_Pass_1_Conc | TDSᵃ_adjustment_Pass_1_Feed | TDSᵃ_adjustment_RO_Pass_1_Conc | Ionic_Strength_Pass_1_Feed | Ionic_Strength_RO_Pass_1_Conc | HCO₃⁻_Pass_1_Feed | HCO₃⁻_RO_Pass_1_Conc | CO₂_Pass_1_Feed | CO₂_RO_Pass_1_Conc | CO₃⁻²_Pass_1_Feed | CO₃⁻²_RO_Pass_1_Conc | CaSO₄_saturation_Pass_1_Feed | CaSO₄_saturation_RO_Pass_1_Conc | BaSO₄_saturation_Pass_1_Feed | BaSO₄_saturation_RO_Pass_1_Conc | SrSO₄_saturation_Pass_1_Feed | SrSO₄_saturation_RO_Pass_1_Conc | CaF₂_saturation_Pass_1_Feed | CaF₂_saturation_RO_Pass_1_Conc | SiO₂_saturation_Pass_1_Feed | SiO₂_saturation_RO_Pass_1_Conc | Mg(OH)₂_saturation_Pass_1_Feed | Mg(OH)₂_saturation_RO_Pass_1_Conc
WAVE_Report_PV1_ELS1_Pressure20.xls | 7.9 | 7.9 | 0.00 | 0.19 | -0.49 | -0.40 | 10,001 | 12,805 | 0.20 | 0.25 | 54.08 | 69.27 | 0.56 | 0.71 | 1.36 | 2.04 | 5.0 | 6.8 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 12.5 | 16.3 | 0.21 | 0.25
WAVE_Report_PV1_ELS2_Pressure10.xls | 7.9 | 7.9 | 0.00 | 0.10 | -0.49 | -0.44 | 10,001 | 11,244 | 0.20 | 0.22 | 54.08 | 61.19 | 0.56 | 0.63 | 1.36 | 1.67 | 5.0 | 5.9 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 12.5 | 14.2 | 0.21 | 0.23
WAVE_Report_PV1_ELS2_Pressure20.xls | 7.9 | 7.8 | 0.00 | 0.36 | -0.49 | -0.32 | 10,001 | 16,114 | 0.20 | 0.32 | 54.08 | 87.30 | 0.56 | 0.90 | 1.36 | 2.98 | 5.0 | 9.1 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 12.5 | 20.8 | 0.21 | 0.28
WAVE_Report_PV1_ELS3_Pressure10.xls | 7.9 | 7.9 | 0.00 | 0.14 | -0.49 | -0.42 | 10,001 | 11,753 | 0.20 | 0.23 | 54.08 | 64.20 | 0.56 | 0.65 | 1.36 | 1.81 | 5.0 | 6.3 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 12.5 | 14.9 | 0.21 | 0.24
WAVE_Report_PV1_ELS3_Pressure20.xls | 7.9 | 7.8 | 0.00 | 0.49 | -0.49 | -0.26 | 10,001 | 19,593 | 0.20 | 0.39 | 54.08 | 106.5 | 0.56 | 1.13 | 1.36 | 4.11 | 5.0 | 11.7 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 12.5 | 25.5 | 0.21 | 0.29

## utility_costs
SourceFile | Non_prod_feed_water_pass1_Flow | Non_prod_unit_cost | Non_prod_hourly_cost | Non_prod_daily_cost | Waste_water_feed_water_pass1_Flow | Waste_water_unit_cost | Waste_water_hourly_cost | Waste_water_daily_cost | Total_service_water_cost
WAVE_Report_PV1_ELS1_Pressure20.xls | 1.6 | 0.1400 | 0.23 | 5.46 | 1.6 | 0.6900 | 1.12 | 26.93 | 32.39
WAVE_Report_PV1_ELS2_Pressure10.xls | 1.9 | 0.1400 | 0.26 | 6.20 | 1.9 | 0.6900 | 1.27 | 30.58 | 36.78
WAVE_Report_PV1_ELS2_Pressure20.xls | 1.3 | 0.1400 | 0.18 | 4.30 | 1.3 | 0.6900 | 0.88 | 21.21 | 25.51
WAVE_Report_PV1_ELS3_Pressure10.xls | 1.8 | 0.1400 | 0.25 | 5.91 | 1.8 | 0.6900 | 1.21 | 29.11 | 35.02
WAVE_Report_PV1_ELS3_Pressure20.xls | 1.0 | 0.1400 | 0.15 | 3.50 | 1.0 | 0.6900 | 0.72 | 17.23 | 20.73

## electricity_details
SourceFile | Peak_Power | Energy | Electricity_unit_cost | Electricity_cost | Specific_Energy
WAVE_Report_PV1_ELS1_Pressure20.xls | 1.5 | 35.1 | 0.09 | 3.2 | 3.11
WAVE_Report_PV1_ELS2_Pressure10.xls | 0.7 | 17.5 | 0.09 | 1.6 | 2.92
WAVE_Report_PV1_ELS2_Pressure20.xls | 1.5 | 35.1 | 0.09 | 3.2 | 1.78
WAVE_Report_PV1_ELS3_Pressure10.xls | 0.7 | 17.5 | 0.09 | 1.6 | 2.15
WAVE_Report_PV1_ELS3_Pressure20.xls | 1.5 | 35.1 | 0.09 | 3.2 | 1.38

## pump_details
SourceFile | Feed_Flow_rate | Feed_Power | Feed_Energy | Feed_Cost | Pass_1_Total_Flow_rate | Pass_1_Total_Power | Pass_1_Total_Energy | Pass_1_Total_Cost | System_Total_Flow_rate | System_Total_Power | System_Total_Energy | System_Total_Cost
WAVE_Report_PV1_ELS1_Pressure20.xls | 2.10 | 1.46 | 35.08 | 3.16 |  | 1.46 | 35.08 | 3.16 |  | 1.46 | 35.08 | 3.16
WAVE_Report_PV1_ELS2_Pressure10.xls | 2.10 | 0.73 | 17.54 | 1.58 |  | 0.73 | 17.54 | 1.58 |  | 0.73 | 17.54 | 1.58
WAVE_Report_PV1_ELS2_Pressure20.xls | 2.10 | 1.46 | 35.08 | 3.16 |  | 1.46 | 35.08 | 3.16 |  | 1.46 | 35.08 | 3.16
WAVE_Report_PV1_ELS3_Pressure10.xls | 2.10 | 0.73 | 17.54 | 1.58 |  | 0.73 | 17.54 | 1.58 |  | 0.73 | 17.54 | 1.58
WAVE_Report_PV1_ELS3_Pressure20.xls | 2.10 | 1.46 | 35.08 | 3.16 |  | 1.46 | 35.08 | 3.16 |  | 1.46 | 35.08 | 3.16

## chemical_details
SourceFile | Total_chemical_cost_per_unit | Total_chemical_cost_per_Dose | Total_chemical_cost_per_volume | Total_chemical_cost_per_total_cost
WAVE_Report_PV1_ELS1_Pressure20.xls |  |  |  | 0.0
WAVE_Report_PV1_ELS2_Pressure10.xls |  |  |  | 0.0
WAVE_Report_PV1_ELS2_Pressure20.xls |  |  |  | 0.0
WAVE_Report_PV1_ELS3_Pressure10.xls |  |  |  | 0.0
WAVE_Report_PV1_ELS3_Pressure20.xls |  |  |  | 0.0

## final_costs
SourceFile | Utility_Chemical_Cost | Specific_Water_Cost
WAVE_Report_PV1_ELS1_Pressure20.xls | 35.6 | 3.142
WAVE_Report_PV1_ELS2_Pressure10.xls | 38.4 | 6.352
WAVE_Report_PV1_ELS2_Pressure20.xls | 28.7 | 1.461
WAVE_Report_PV1_ELS3_Pressure10.xls | 36.6 | 4.464
WAVE_Report_PV1_ELS3_Pressure20.xls | 23.9 | 0.942